样品承认书(Specification)

客户名称(Customer) :

品    名(Part Name):   DC Brushless Fan

规格型号(Model No.):   RD8038B48L-A

样品数量(Quantity) ：

日    期(Date)    ：     2015-11-14

客户承认签章 CUSTOMER APPROVED

SUPPLIER：三河市科丰电气有限公司

ADD：-

TEL：010-80843596

Website：http://www.cnecport.com/

| APPROVED |  | CHECKED |  | PREPARED |  |
| --- | --- | --- | --- | --- | --- |

表格编号：RUNDA-QR-JS04A/1

1.General Specification

| 项目Item | 描述Description | 测试条件Condition |
| --- | --- | --- |
| 1-1. 外形尺寸Dimension | 80x80x38mm |  |
| 1-2. 轴承 Bearing Type | 双滚珠轴承 Two Ball Bearing |  |
| 1-3. 额定电压Rated Voltage | DC48V |  |
| 1-4. 操作电压Operating Voltage | DC 35V~58V |  |
| 1-5. 启动电压Start-up Voltage | 35V | 25℃ Power ON/OFF |
| 1-6 额定电流Rated Current Current | 0.06(Max:0.07)A | A.At Rated Voltage B.25℃ C.65%RH D.Measured after 5minutes |
| 1-7. 额定功率Rated Power Power | 2.88(Max:3.36)W |  |
| 1-8. 额定转速Rated Speed | 3200rpm/min±10% |  |
| 1-9. 最大风量Max. Air Flow | 39.99( Min:35.99)CFM | PQ Measurement Apparatus Standard: AMCA Rated Voltage Rated Current |
|  | 1.13( Min:1.02m3/min ) |  |
| 1-10. 最大静压Max.Static Pressure | 5.17(Min:4.19)mm-H2O |  |
|  | 0.20(Min:0.16)inch-H2O |  |
| 1-11. 噪音Noise level | 34.5(Max:36.23)dBA | Rated Voltage Mute Room Distance:1M Background Noise: <18dB |
| 1-12. 寿命预估Life Expectance | 70000hrs at 40℃ 相对湿度15%～65%RH | L10 Failure Criteria: A.Speed:Under15% of original value B.Current:Over15% of original value C. Fan not run |
| 1-13. 马达极数Pole | 4 Poles |
| 1-14. 旋转方向Rating Direction | Anticlockwise |
| 1-15.其他特点Other Features | Tachometer Output 测速计输出 | ○ |
|  | Lock Rotor Alarm 锁定报警 | ○ |
|  | LD Rotor Alarm 寿命告警 | ○ |
|  | Auto start 自动重启 | ● |
|  | Soft Start 软启动 | ○ |
|  | Speed Control Mode 速度控制模式 | ○ |
|  | Protection level 防护等级 | ○ |

2.Electrical Specification

| 项目Item | 条件Condition |
| --- | --- |
| 2-1.锁定扇叶保护功能 Locked Rotor Protection | ○安规条件 Safety Condition |
|  | ●额定电压下风扇被锁定1-3秒时，自动断电，并在2至6秒内自动尝试启动，锁住扇叶72小时无损坏。Auto power off after locked at rated voltage for 1-3sec. And then circuit attempt to restart in 2 to 6 sec，There is no damage after 72hours locking。 |
| 2-2.极性保护 Polarity Protection | ●Vcc与GND反接时，不导通 Open circuit when Vcc&GND are exchanged |
|  | ○ Vcc与GND反接时，5秒内不烧毁 Circuit won't be burned within 5seconds when Vcc&GND are exchanged |
| 2-3.绝缘阻抗 Insulation Resistance | At least 10MΩ at 500 VDC between housing and both lead wires |
| 2-4.绝缘耐压 Dielectric strength | Withstand 500 VAC 1 minute 1mA between housing and both lead wires |

3.Specification of Main Material

| 3-1.外框材质 Frame | PBT UL94V-0 |
| --- | --- |
| 3-2.扇叶材质 Propeller | PBT UL94V-0 |
| 3-3.绝缘架 Bobbin | PBT UL94V-0 |
| 3-4.导线 Lead wires | Red(+),Black(-) UL1007#22AWG, 300±5mm |
| 3-5.端子 Connector | None |
| 3-6商标 Lable Marking | 型号/Model No:RD8038B48L-A 额定电压/Rated Voltage：DC 48V 安规电流/Rated Current： 0.8A |

4.Environmental Specification

| 项目 Item | 条件 Condition |
| --- | --- |
| 4-1.运转温度，湿度范围 Operating Temp. Humidity Range | Temperature: -10~+70℃ |
|  | Humidity :15%~90%RH |
| 4-2.保存温度，湿度范围 Storage Temp. Range | Temperature: -20~+85℃ |
|  | Humidity :15%~90%RH |

5.P-Q特性曲线测试(P-Q Characteristic curve test)：

| 测试条件及方法（ Test conditions and methods） |
| --- |
| 测试方法（Testing Method ）：恒定电压测试 Constant Voltage |
| 大气压力（Barometric Pressure）：752.4 mmHg | 额定电压 At Rated Voltage |
| 相对 湿度（Relative Humidity）：66.825% | 测试温度（Temperature）：25° |
| 测试数据（test data ）： Max Ps :5.17 mmAq Max Flow Rate :39.99 CFM |

6. Noise Test（噪音测试）

| 测试条件 Test Condition | 测试方法 Test Method |
| --- | --- |
| 1.温度 Temperature： 26 ℃ | 1.测试位置 Test Postion：180º |
| 2.湿度 Humidity： 62 %RH | 2.测试距离 Test Distance：1.0M From the fan intake |
| 3.额定电压 At Rated Voltage: 48V DC |  |
| 4.额定转速 At Rated Speed: 3200 RPM | 3.背景噪音 Background Noise：14.56dB(A) |
|  | 4.测试依照标准 ISO3745执行 This test executes to ISO3745 standard |
| 测试设备 Test Equiprment： AW6269双通道噪音频谱分析仪 AW6269 double channels noise Spectrum Analyzer |
| 测试结果 Test Result： 噪音:34.5分贝； Leq:34.5dB(A) |

6-1.噪音测试方法示意图（Schematic diagram of noise test method）：

风向

7.尺寸图Dimension Drawing

8.Note:

8-1. 使用时请勿超出本规格所规定之极限，否则我们不保证此产品。

We will not guarantee the products if the application of our products are exceeded the limitation which is specified on this specification.

8-2.倘若要变更此份文件的任何规格，请务必事先提出需求。

In case of changes of the specification specified on this document.A written notice is requested in advance.

8-3.请勿触压着叶片以及电源线缠绕着风扇或用用拉扯电源线，如此轴心与电源线将会被损毁。

Please do not touch the impeller with the pressure and never bring the fan with lead wire.The bearing and lead wire may be damaged.

8-4. 本产品不保证因小虫进入，而影响寿命与不良品产生。

No guarantee on the products against the safety problem or failure caused by insect.

8-5.如有任何资料及文件与此份资料不同，将以此份资料为主要参考。

If there is any data or related documentation different from this data sheet.This data sheet is the principle reference.

8-6.请勿在可燃性气体与任何有害环境中使用。

Please do not use the fan in the environment of corrosive gas or liquid or any detrimental gas.

8-7.组装风扇时，请特别注意，因共振或振动产生的噪音。

During the installation of the fan, please pay substantial attention to possible notice caused by resonance vibration and shock.

8-8.当搬运或作业中，风扇如从60cm的高度落下，将会对叶片的平衡产生若干影响，特别是滚珠轴承避免掉落。

It is very important to notify that avoid to drop from 60cm height when in any movement or operation,it will impact the balance of blade. Especially ball bearing structure is avoided to drop down.

8-9.锁外壳之螺丝扭力不得超 4Kgf。

The torque of the screw which locked the frame should not exceed 4 Kgf.

8-10.当风扇在运转时，请不要触摸叶片，这样非常危险，容易伤害到您的手指。

Please don’t touch the blade when the fan at full speed running , be careful your fingers!

# Text boxes

DC FAN

MICROPHONE

1M